08 71 00

Door Hardware

2.xx		EXIT DEVICES (Value Series)

- General

1.	Durable design for use on primary and secondary doors.

2.	Extended warranty:

a.	Ten year manufacturer's  limited warranty on mechanical functions.

b.	Three year manufacturer's limited warranty on electrical components.

3.	Modern push pad design.

4.	Provide with machine and self drilling screw fasteners unless otherwise  specified or required by door construction.

5.	Minimal door preparation. No mortising required for outside trim.

B.	Standards Compliance

1.	BHMA certified for conformance to:

a.	Grade 1 requirements of ANSI/BHMA A156.3 American National 					Standard for Exit Devices.

2.	Conform to requirements of:

a.	National Fire Protection Association Life Safety Code, NFPA 				101.

b.	ICC/ANSI A.117.1 Accessible and Usable Buildings and Facilities.

c.	California Title 19.

d.	Americans with Disabilities Accessibility Guidelines.

e.	Miami-Dade County NOA 05-0810.04 for wind and hurricane 				rated doors

3.	U.L. and U.L.C. listed

a.	Panic hardware

b.	 Fire exit hardware when used on fire rated doors.

C.	Material

1.	Exposed surfaces: High impact ABS and anodized aluminum.

2.	Latchbolt: Stainless steel

D.	Features

1.	Mounting plate and strike locator system for simple, accurate, and fast installation without paper templates.

2.	End cap: Angled to protect end of device

3.	Non-handed

4.	Dogging: 1/8 turn hex key standard

5.	Available for 36' or 48" door widths

a.	Field sizeable for other widths.

6.	Provide narrow stile application where specified or required because of stile width.

7.	Functions contained in outside trim allow changing function without removing device from the door.

E.		Functions

1	01: Exit only, No trim

2.	02: Dummy trim, no cylinder.

3.	03: Entrance by trim when latchbolt is retracted by key. Key removable only when locked. Rim cylinder required

4.	08: Entrance by lever. Key locks or unlocks lever. Mortise cylinder required.

5.	14: Entrance by lever. Lever operable at all times. No cylinder.

F.	Trim

1.	Outside trims easily changed or re-keyed without removing device from 		door.

2.	Wide stile standard. Provide narrow stile option where specified or 	required by door stile width.

a.	Minimum stile width with surface strike: 4-5/8".

b.	Minimum stile width with semi mortise strike: 4-1/8"

c.	Include disengaging clutch mechanism to prevent damage when excess force is applied.

3.	Trim design: Match design specified for locksets unless otherwise 		specified.

G.	Finish

1.	Device: Choice of

a.	BHMA 628:	Clear anodized aluminum

b.	BHMA 711:	Black anodized aluminum.

2.	Trims

a.	P & PN designs: BHMA 628 Clear anodized aluminum.

b.	WS design: BHMA 626 Brushed chrome.

c.	A, AN, and BN designs: BHMA 689 Powder coated aluminum.

H.	Rim Device

1.	ANSI/BHMA A156.3 Type 1.

2.	Series: V40

3.	Latchbolt: deadlocking, Pullman type.

4.	Back plate: Steel, corrosion resistant.

5.	Fire rated door assemblies: provide fire exit hardware device.

a	U.L listed for 3 hour fire rated door assemblies.

1)	Single doors up to 4' 0" wide x 10' 0" high.

2)	Pairs of doors with fire rated mullion up to 8' x 8'.

6.	For doors subject to hurricane strength winds, provide device with hurricane rating conforming to Dade County code requirements.

I.	Optional Features. Provide where specified or required.

1.	Cylinder dogging: Suffix CD

2.	Hurricane (Wind Rated): Prefix H

3.	Hurricane and fire rated: Suffix FH

4.	Key stop: Suffix KS

5.	Less dogging: Suffix LD

6.	Fire exit hardware: Prefix F

7.	Glass bead kit.

8.	Sex nut kit

9.	Security Torx© screw kit.

J.	Accessories

1	Removable mullions

a.	Provide where specified or required for pairs of doors..

b.	Keyed removable

1).	Provide rim cylinder

c.	Provide fire rated mullions for use on fire rated door assemblies.

K.		Exit Alarm Options

1.	Battery Powered (EB)

a.	Standard features

1)  	Switch monitors push pad.

2)  	Green and Red LED's for arming indication.

3)	Cylinder arming.

4)	9 volt battery and Piezo horn.

5)	Cylinder dogging except for fire exit hardware.			6)	Push pad signage

7)	Red push pad

b.	Additional requirements when specified

1)	Key stop feature

2)	Less dogging

3)	Black Push pad

4)	Latch bolt monitoring switch

5)	Weatherized (EB-W)

2.	Hardwired (EH)

a.	Standard features

1)  	Switch monitors push pad.

2)  	Green and Red LED's for arming indication.

3)	Cylinder arming.

4)	9 volt battery back up

5)	Piezo horn.

6)	Cylinder dogging except for fire exit hardware.			7)	Push pad signage

8)	Red push pad

9)	Flexible 3' conduit loop and end cap connector

10)	120v to 12 vac transformer

b.	Additional requirements when specified

1)	Key stop feature

2)	Less dogging

3)	Black Push pad

4)	Latch bolt monitoring switch

5)	Weatherized (EB-W)

6)	220v to 24 vac transformer

7)	277v to 24 vac transformer

8)	Power transfer

9)	Remote signal (EH-R)

L.	Electrified Operation Options

1.	Electric Dogging (ED):

a.	Standard features

1)  	On-board switching requires initial push pad depression after 				electric activations..

2)  	Capable of long term dogging.

3)	Requires Logic controller and power supply

b.	Additional requirements when specified

1)	24VAC transformer (Type PP-5152-2)

2)	Logic controller for filtered, regulated power supply and 				simplified fire loop connections.(Type 80-800)

3)	Flexible conduit and end cap.

4)	Power Transfer

5)	Request to exit switching.

2	Electric Latch Retraction (ER):

a.	Standard features.

1)	Simultaneous latch and push pad retraction.

2)	Long term dogging capability.

3)	Switches to monitor push pad, latch bolt, and outside trim 					input.

4)	Requires Logic controller and power supply

b.	Additional requirements when specified

1)	Logic controller and power supply for filtered, regulated 				power supply and electric latch retraction (Type 81-800, 82-				800, or 83-800) .

2)	Flexible conduit and end cap.

3)	Power Transfer

4)	Request to exit switching

3.	Electric Integration (EI):

a.	Standard features

1)  	Switches to monitor push pad, latch bolt, and outside trim 				input.

2)	Green and Red LED's for arming indication.

3)	Cylinder arming.

4)	Piezo horn (logic and power supply separate)

5)	Cylinder dogging except for fire exit hardware.

5)	Code compliant signage

6)	Requires Logic controller and power supply

b.	Additional requirements when specified

1)	Logic controller and power supply for filtered, regulated				power supply and electronic integration. (Type 10-800 or 11-				800).

2)	Flexible conduit and end cap.

3)	Power Transfer

4)	Key stop feature

5)	Less dogging.

6)	Red Push pad

4.	Electric switching (ES)

a.	Standard features.

1)	Switches to monitor push pad, latch bolt, and outside trim 					input.

2)	Hex key dogging standard except for fie exit hardware.

3)	Black push pad

b.	Additional requirements when specified

1)	Flexible conduit and end cap.

2)	Power Transfer

3)	Cylinder dogging.

4)	Less dogging.

5)	Red push pad

5.	Request to Exit Switching (EX)

a.	Standard features.

1)	Switch monitors push pad.

2)	Hex key dogging standard except for fie exit hardware.

3)	Black push pad

b.	Additional requirements when specified

1)	Flexible conduit and end cap.

2)	Power Transfer

3)	Cylinder dogging.

4)	Less dogging.

5)	Red push pad

6.	Request to Exit Switching - Weatherized (EX-W)

a.	Standard features.

1)	Weatherized switch monitors push pad.

2)	Hex key dogging standard except for fie exit hardware.

3)	Black push pad

b.	Additional requirements when specified

1)	Flexible conduit and end cap.

2)	Power Transfer

3)	Cylinder dogging.

4)	Less dogging.

5)	Red push pad

M.	Electrified Delayed Egress Options

1.	General:

a.	Conform to the special locking requirements of the National Fire 				Protection Association Life Safety Code, NFPA 101

2.	Delayed Egress (EE)

a.	Standard Features

1)	Self contained delayed egress system.

2)	15 second delayed egress with latch bolt security monitoring.

3)	Regulated, filtered power supply.

4)	On-board logic controller.

5)	Switches monitor push pad, latch bolt, and outside trim input.

6)	Cylinder dogging except for fire exit hardware.

7)	Self adhesive code compliant door sign

b.	Additional requirements when specified

1)	Power supply less transformer

2)	Less power supply

3)	30 second delay

4)	Flexible conduit and end cap.

5)	Power Transfer

6)	Less dogging.

7)	Substitute door signage

8)	Key stop

9)	Black push pad

3	.Delayed Egress with Magnetic Lock (EM)

a.	Standard Features

1)	15 second delayed egress with latch bolt security monitoring.

2)	Regulated, filtered power supply.

3)	.Cylinder dogging except for fire exit hardware.

4)	Magnetic Lock

5)	Self adhesive code compliant door sign

6)	Flexible conduit and end cap

b.	Additional requirements when specified

1)	Power supply less transformer

2)	Less power supply

3)	30 second delay

4)	Black push pad.

5)	Power Transfer

6)	Less dogging.

7)	Substitute door signage

8)	Key stop feature

:

N.	Electrified Accessories

1.	Provide where specified or required for complete system.

a.	Controllers and Power Supplies

b.	Battery and battery box for controllers

c.	Cover locks and keys

O.	Manufacturer:

1.	Detex Corporation

302 Detex Drive

New Braunfels, Texas 78130-3045 USA

Phone: (800) 729-3839

Fax: (800) 653-3839

www.detex.dom

marketing@detexcorp.com